{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":11,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DV3P-H"]
[]
[]
[]
[]
["","","","","","EWAA004D2V3P-H","EWAA006D2V3P-H","EWAA008D2V3P-H","EWAA011DAV3P-H-","EWAA014DAV3P-H-","EWAA016DAV3P-H-"]
["Kylkapacitet","Nom.","","","kW","4.86 (1), 4.52 (2)","5.83 (1), 5.09 (2)","6.18 (1), 5.44 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Kapacitetsstyrning","Metod","","","","Variabel (inverter)","Variabel (inverter)","Variabel (inverter)","Variabel (inverter)","Variabel (inverter)","Variabel (inverter)"]
["Ineffekt","Kyla","","Nom.","kW","0.820 (1), 1.36 (2)","1.08 (1), 1.55 (2)","1.19 (1), 1.73 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["EER","","","","","5.91 (1), 3.32 (2)","5.40 (1), 3.28 (2)","5.19 (1), 3.14 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["SEER","","","","","","","","5.79 (5)","5.71 (5)","5.59 (5)"]
["Mått","Enhet","","Djup","mm","362","362","362","460","460","460"]
["","","","Höjd","mm","770","770","770","870","870","870"]
["","","","Bredd","mm","1250","1250","1250","1380","1380","1380"]
["Vikt","Enhet","","","kg","88","88","88","147","147","147"]
["Hölje","Färg","","","","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit"]
["","Material","","","","Förzinkat stål","Förzinkat stål","Förzinkat stål","Polyestermålad galvaniserad stålplåt","Polyestermålad galvaniserad stålplåt","Polyestermålad galvaniserad stålplåt"]
["Luftvärmeväxlare","Typ","","","","","","","Högeffektiv fläns- och rörtyp med integrerad underkylare","Högeffektiv fläns- och rörtyp med integrerad underkylare","Högeffektiv fläns- och rörtyp med integrerad underkylare"]
["Fläkt","Antal","","","","1","1","1","1","1","1"]
["","Typ","","","","Propellerfläkt","Propellerfläkt","Propellerfläkt","Propellerfläkt","Propellerfläkt","Propellerfläkt"]
["Fläktmotor","Drivning","","","","","","","Direktdriven","Direktdriven","Direktdriven"]
["Kompressor","Kvantitet_","","","","1","1","1","1","1","1"]
["Kompressor","Typ","","","","Hermetiskt tillsluten swing-kompressor","Hermetiskt tillsluten swing-kompressor","Hermetiskt tillsluten swing-kompressor","Hermetiskt tillsluten swing inverterkompressor","Hermetiskt tillsluten swing inverterkompressor","Hermetiskt tillsluten swing inverterkompressor"]
["Kompressor","Startmetod_","","","","","","","Omformardriven","Omformardriven","Omformardriven"]
["Driftsområde","Omgivande luft","Kyla","Min.","°CDB","10 (3)","10 (3)","10 (3)","10","10","10"]
["","","","Max.","°CDB","43","43","43","43","43","43"]
["","Vattensida","Förångare","Min.","°CDB","5 (3)","5 (3)","5 (3)","5","5","5"]
["","","","Max.","°CDB","22","22","22","22","22","22"]
["Ljudeffektsnivå","Kyla","","Nom.","dBA","61","62","62","67.0","69.0","69.0"]
["Ljudtrycksnivå","Kyla","","Nom.","dBA","48","49","50","47.7","50.8","51.0"]
["Köldmedium","Typ","","","","R-32","R-32","R-32","R-32","R-32","R-32"]
["","GWP","","","","675","675","675","675.0","675.0","675.0"]
["","Mängd","","","kg","1.35","1.35","1.35"]
["","Kretsar","","Kvantitet","","","","","1","1","1"]
["Strömförsörjning","Fas","","","","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Spänning","","","V","230 +/-10%","230 +/-10%","230 +/-10%","230","230","230"]
["","Spänningsområde","","Min.","%","","","","-10","-10","-10"]
["","","","Max.","%","","","","10","10","10"]
["Enhet","Belastningsström","","Max","A","","","","30.8","30.8","30.8"]
["Anm:","","","","","(1) - Tillstånd 1: kyla Ta 35 °C - LWE 18 °C (DT = 5 °C); värme Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(1) - Tillstånd 1: kyla Ta 35 °C - LWE 18 °C (DT = 5 °C); värme Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(1) - Tillstånd 1: kyla Ta 35 °C - LWE 18 °C (DT = 5 °C); värme Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(1) - Kyla: EW 12°C; LW 7°C; omgivningsförhållanden: 35 °CTT","(1) - Kyla: EW 12°C; LW 7°C; omgivningsförhållanden: 35 °CTT","(1) - Kyla: EW 12°C; LW 7°C; omgivningsförhållanden: 35 °CTT"]
["","","","","","(2) - Tillstånd 2: kyla Ta 35 °C - LWE 7℃ (DT = 5 °C); värme Ta DB/WB 7 °C/6 °C - LWC 45℃ (DT = 5 °C)","(2) - Tillstånd 2: kyla Ta 35 °C - LWE 7℃ (DT = 5 °C); värme Ta DB/WB 7 °C/6 °C - LWC 45℃ (DT = 5 °C)","(2) - Tillstånd 2: kyla Ta 35 °C - LWE 7℃ (DT = 5 °C); värme Ta DB/WB 7 °C/6 °C - LWC 45℃ (DT = 5 °C)","(2) - Kyla: EW 23°C; LW 18°C; omgivningsförhållanden: 35 °CTT","(2) - Kyla: EW 23°C; LW 18°C; omgivningsförhållanden: 35 °CTT","(2) - Kyla: EW 23°C; LW 18°C; omgivningsförhållanden: 35 °CTT"]
["","","","","","(3) - För mer information se driftsområdesritning","(3) - För mer information se driftsområdesritning","(3) - För mer information se driftsområdesritning","(3) - I enlighet med EN14825","(3) - I enlighet med EN14825","(3) - I enlighet med EN14825"]
["","","","","","","","","(4) - Beroende på driftläge, se installationsmanualen.","(4) - Beroende på driftläge, se installationsmanualen.","(4) - Beroende på driftläge, se installationsmanualen."]