{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":13,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-TZSLC2"]
[]
[]
[]
[]
["","","","","","EWADH12TZSLC2","EWADC15TZSLC2","EWADH11TZSLC2","EWADH17TZSLC2","EWADC16TZSLC2","EWADH13TZSLC2","EWADH19TZSLC2","EWADH18TZSLC2"]
["Kylkapacitet","Nom.","","","kW","1,259","1,508","1,189","1,766","1,644","1,355","1,965","1,875"]
["Effektstyrning","Metod","","","","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel"]
["","Minimikapacitet","","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Ineffekt","Kyla","","Nom.","kW","413.4","485","380.9","581.8","532.8","438.6","709.3","636.4"]
["EER","","","","","3.05","3.11","3.12","3.04","3.09","3.09","2.77","2.95"]
["IPLV","","","","","4.8","5.14","4.85","5.07","5.11","4.78","4.99","5.04"]
["SEER","","","","","4.64","4.83","4.69","4.86","4.87","4.65","4.68","4.83"]
["Mått","Enhet","","Djup","mm","10,510","11,404","10,510","13,202","12,302","11,404","14,102","14,102"]
["","","","Höjd","mm","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540"]
["","","","Bredd","mm","2,282","2,282","2,282","2,282","2,282","2,282","2,282","2,282"]
["Vikt","Arbetsvikt","","","kg","9,879","11,727","9,879","12,575","12,145","11,123","13,048","13,048"]
["","Enhet","","","kg","9,322","10,716","9,322","11,564","11,134","10,112","12,037","12,037"]
["Hölje","Färg","","","","Elfenbensvit_","Elfenbensvit_","Elfenbensvit_","Elfenbensvit_","Elfenbensvit_","Elfenbensvit_","Elfenbensvit_","Elfenbensvit_"]
["","Material","","","","Galvaniserad och målad stålplåt","Galvaniserad och målad stålplåt","Galvaniserad och målad stålplåt","Galvaniserad och målad stålplåt","Galvaniserad och målad stålplåt","Galvaniserad och målad stålplåt","Galvaniserad och målad stålplåt","Galvaniserad och målad stålplåt"]
["Luftvärmeväxlare","Typ","","","","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel"]
["Fläkt","Antal","","","","22","24","22","28","26","24","30","30"]
["","Typ","","","","Direktdriven propeller","Direktdriven propeller","Direktdriven propeller","Direktdriven propeller","Direktdriven propeller","Direktdriven propeller","Direktdriven propeller","Direktdriven propeller"]
["Fläktmotor","Drivning","","","","PÅ/AV","PÅ/AV","PÅ/AV","PÅ/AV","PÅ/AV","PÅ/AV","PÅ/AV","PÅ/AV"]
["Compressor","Kvantitet_","","","","2","2","2","2","2","2","2","2"]
["","Typ","","","","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor"]
["","Starting method","","","","VFD-driven","VFD-driven","VFD-driven","VFD-driven","VFD-driven","VFD-driven","VFD-driven","VFD-driven"]
["Sound power level","Kyla","","Nom.","dBA","100","101","100","102","101","101","103","103"]
["Ljudtrycksnivå","Kyla","","Nom.","dBA","78","78","77","79","79","78","80","79"]
["Köldmedium","Typ","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Charge","","","kg","175","200","175","250","220","200","270","270"]
["","Kretsar","","Kvantitet","","2","2","2","2","2","2","2","2"]
["Röranslutningar","Evaporatorvatten inlopp/utlopp (YD)","","","","219.1","273","219.1","273","273","273","273","273"]
["Power supply","Fas","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Spänning","","","V","400","400","400","400","400","400","400","400"]
["","Spänningsområde","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10"]
["Enhet","Startström","","Max","A","0","0","0","0","0","0","0","0"]
["","Belastningsström","Kyla","Nom.","A","691.1","813.9","646.5","962.8","884.0","733.0","1,149","1,044"]
["","","","Max","A","969","1,165","913","1,301","1,205","1,027","1,487","1,398"]
["","Maximal anläggningsström för dimensionering av kablar","","","A","1,066","1,282","1,004","1,431","1,326","1,130","1,636","1,538"]