{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":13,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYS-4ZXR"]
[]
[]
[]
[]
["","","","","","EWYS4004ZXRB2","EWYS4504ZXRB2","EWYS5004ZXRB2","EWYS5504ZXRB2","EWYS6004ZXRB2","EWYS6504ZXRB2","EWYS7004ZXRB2","EWYS8004ZXRB2"]
["Kylkapacitet","Nom.","","","kW","350.3","380.8","434.2","485","534.3","578.4","613.2","672.3"]
["Kapacitetsstyrning","Metod","","","","Steglös","Steglös","Steglös","Steglös","Steglös","Steglös","Steglös","Steglös"]
["Effektstyrning","Minimikapacitet","","","%","20","18","17","14","14","13","12","11"]
["Ineffekt","Kyla","","Nom.","kW","121.21","137.97","149.21","175.09","190.14","201.53","212.92","240.97"]
["EER","","","","","2.89","2.76","2.91","2.77","2.81","2.87","2.88","2.79"]
["SEER","","","","","4.63","4.55","4.78","4.82","5.07","5.15","5.05","5.13"]
["Mått","Enhet","","Djup","mm","5825","5825","6725","6725","7625","8525","8525","8525"]
["","","","Höjd","mm","2465","2465","2465","2465","2465","2465","2465","2465"]
["","","","Bredd","mm","2285","2285","2285","2285","2285","2285","2285","2285"]
["Vikt","Arbetsvikt","","","kg","6705","6725","7725","7725","9100","9705","11075","11110"]
["","Enhet","","","kg","6240","6260","7035","7035","8015","8600","9690","9715"]
["Hölje","Färg","","","","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit"]
["","Material","","","","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål"]
["Luftvärmeväxlare","Typ","","","","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium"]
["Fläkt","Antal","","","","10","10","12","12","14","16","16","16"]
["","Typ","","","","EC","EC","EC","EC","EC","EC","EC","EC"]
["Kompressor","Kvantitet_","","","","2","2","2","2","2","2","2","2"]
["","Typ","","","","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor"]
["Driftsområde","Vattensida","Förångare","Min.","°CTT","-8","-8","-8","-8","-8","-8","-8","-8"]
["","","","Max.","°CTT","20","20","20","20","20","20","20","20"]
["Ljudeffektsnivå","Kyla","","Nom.","dBA","88","87","88","88","89","89","91","91"]
["Ljudtrycksnivå","Kyla","","Nom.","dBA","67","66","67","67","68","67","69","69"]
["Köldmedium","Typ","","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","GWP","","","","638","639","640","641","642","643","644","645"]
["","Mängd","","","kg","198","198","198","198","198","198","198","198"]
["","Kretsar","","Kvantitet","","2","2","2","2","2","2","2","2"]
["Röranslutningar","Evaporatorvatten inlopp/utlopp (YD)","","","","219.1","219.1","219.1","219.1","219.1","219.1","219.1","219.1"]
["Strömförsörjning","Fas","","","","3","3","3","3","3","3","3","3"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Spänning","","","V","400","400","400","400","400","400","400","400"]
["","Spänningsområde","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","+10","+10","+10","+10","+10","+10","+10","+10"]
["Enhet","Startström","","Max","A","0","0","0","0","0","0","0","0"]
["","Belastningsström","Kyla","Nom.","A","228","253","274","329","340","360","388","431"]
["","","","Max","A","335","374","396","451","473","524","550","656"]
["","Maximal anläggningsström för dimensionering av kablar","","","A","369","411","436","496","520","576","605","722"]