{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":13,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYS-4ZXS"]
[]
[]
[]
[]
["","","","","","EWYS4004ZXSB2","EWYS4504ZXSB2","EWYS5004ZXSB2","EWYS5504ZXSB2","EWYS6004ZXSB2","EWYS6504ZXSB2","EWYS7004ZXSB2","EWYS8004ZXSB2"]
["Kylkapacitet","Nom.","","","kW","393.1","440.8","495.2","532.1","584.5","644.4","682.5","765.7"]
["Kapacitetsstyrning","Metod","","","","Steglös","Steglös","Steglös","Steglös","Steglös","Steglös","Steglös","Steglös"]
["Effektstyrning","Minimikapacitet","","","%","17","15","15","13","13","12","11","10"]
["Ineffekt","Kyla","","Nom.","kW","135.55","151.48","166.73","189.36","196.8","221.44","221.59","256.09"]
["EER","","","","","2.9","2.91","2.97","2.81","2.97","2.91","3.08","2.99"]
["SEER","","","","","4.55","4.55","4.85","4.71","4.91","5.01","5.14","5.11"]
["Mått","Enhet","","Djup","mm","5825","5825","6725","6725","7625","8525","8525","8525"]
["","","","Höjd","mm","2465","2465","2465","2465","2465","2465","2465","2465"]
["","","","Bredd","mm","2285","2285","2285","2285","2285","2285","2285","2285"]
["Vikt","Arbetsvikt","","","kg","6540","6560","7560","7560","8935","9540","10785","10820"]
["","Enhet","","","kg","6075","6095","6870","6870","7850","8435","9405","9430"]
["Hölje","Färg","","","","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit","Elfenbensvit"]
["","Material","","","","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål","Galvaniserat stål"]
["Luftvärmeväxlare","Typ","","","","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium","Högeffektiv fläns- och rörtyp – koppar/aluminium"]
["Fläkt","Antal","","","","10","10","12","12","14","16","16","16"]
["","Typ","","","","EC","EC","EC","EC","EC","EC","EC","EC"]
["Kompressor","Kvantitet_","","","","2","2","2","2","2","2","2","2"]
["","Typ","","","","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor","Inverterdriven enkelskruvkompressor"]
["Driftsområde","Vattensida","Förångare","Min.","°CTT","-8","-8","-8","-8","-8","-8","-8","-8"]
["","","","Max.","°CTT","20","20","20","20","20","20","20","20"]
["Ljudeffektsnivå","Kyla","","Nom.","dBA","99","98","99","99","100","100","102","102"]
["Ljudtrycksnivå","Kyla","","Nom.","dBA","78","77","77","78","78","79","80","80"]
["Köldmedium","Typ","","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","GWP","","","","630","630","630","630","630","630","630","630"]
["","Mängd","","","kg","198","198","198","198","198","198","198","198"]
["","Kretsar","","Kvantitet","","2","2","2","2","2","2","2","2"]
["Röranslutningar","Evaporatorvatten inlopp/utlopp (YD)","","","","219.1","219.1","219.1","219.1","219.1","219.1","219.1","219.1"]
["Strömförsörjning","Fas","","","","3","3","3","3","3","3","3","3"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Spänning","","","V","400","400","400","400","400","400","400","400"]
["","Spänningsområde","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","+10","+10","+10","+10","+10","+10","+10","+10"]
["Enhet","Startström","","Max","A","0","0","0","0","0","0","0","0"]
["","Belastningsström","Kyla","Nom.","A","236","272","293","332","343","378","395","454"]
["","","","Max","A","335","374","396","451","473","524","550","656"]
["","Maximal anläggningsström för dimensionering av kablar","","","A","369","411","436","496","520","576","605","722"]